## 1 Load Calc Table
Appliance | Qty | Each Running Wattage (W) | Total Running Wattage (W) | Surge Wattage (W) | AVG Daily Usage (hours) | Total Energy (Wh) | Essential? | Notes
LED lights | 4 | 20 | 80 |  | 6 | 480 | Y
Plug Loads | 2 | 10 | 20 |  | 2 | 40 | Y | cell phone chargers
Fan | 1 | 100 | 100 | 200 | 4 | 400 | N
LCD TV | 1 | 150 | 150 |  | 2 | 300 | N
Water Pump | 1 | 500 | 500 | 1500 | 0.5 | 250 | Y
|  |  | 0 |  |  | 0 | Y
|  |  | 0 |  |  | 0 | Y
|  |  | 0 |  |  | 0 | Y
Essentials |  |  | 600 | 1500 |  | 770
Non Essentials |  |  | 250 |  |  | 700
TOTAL |  |  | 850 |  |  | 1470
Peak Continuous Power | [5 empty] | 600 | W | Essential Only
Peak Surge Power | [5 empty] | 1500 | W | Maximum Surge
Daily Energy Usage | [5 empty] | 1470 | kWh | Average
Find more details at:
www.OffGridSolarBook.com

## 2 Derate
Component Derate Factors | Range | Entry | Notes
PV module nameplate DC rating | 0.80 – 1.05 | 0.95 | From Spec Sheet
PV Temperature | 0.85 – 1.05 | 0.95 | Site Specific
Soiling | 0.30 – 0.995 | 0.95 | Site Specific
Mismatch | 0.97 – 0.995 | 0.98 | From Spec Sheet
Diodes and connections | 0.99 – 0.997 | 0.99 | Estimation
DC wiring | 0.97 – 0.99 | 0.98 | Estimation
Charge Controller | 0.88 – 0.98 | 0.95 | From Spec Sheet
Battery Round Trip Efficiency | 0.80 – 0.98 | 0.85 | From Spec Sheet
Inverter | 0.88 – 0.98 | 0.92 | From Spec Sheet
AC wiring | 0.98 – 0.993 | 0.99 | Estimation
Shading | 0.00 – 1.00 | 1 | Based on Design, Use 1.0 for no shade
Sun-tracking | 0.95 – 1.00 | 1 | Only for Trackers, Use 1.0 otherwise
Age (~1% per year) | 0.70 – 1.00 | 1 | Based on Design, Use 1.0 for new
DC Derate Factor |  | 0.65826
AC Derate Factor |  | 0.9108
Overall Derate Factor |  | 0.59955

## 3 Input
Site/Location Specifications |  |  |  | Site/Location Requirements
| Entry | Units | Notes |  | Entry | Units | Notes
Location Name | Oakland |  |  | Peak Continuous Power | 600 | W | From Load Calculation Table tab
Celsius or Fahrenheit? | C | °C | Choose C or F | Peak Surge Power | 1500 | W | From Load Calculation Table tab
Extreme Minimum Temp in °C | -4 | °C | Default 0°C | Daily Energy Usage | 1470 | Wh | From Load Calculation Table tab
Racking Type | Pole Mount |  | Choose a type | Overall Derate Factor | 0.59955 |  | From Derate tab
Mininum Winter PSH | 3.05 | hr | http://pvwatts.nrel.gov/pvwatts.php | Required Storage Capacity | 612.9621 | Ah
Maximum Summer PSH | 7.53 | hr | http://pvwatts.nrel.gov/pvwatts.php | Required Storage Capacity | 14711.0906 | Wh
Battery Specifications |  |  |  | Battery Requirements
| Entry | Units | Notes |  | Entry | Units | Notes
Battery Chemistry | VRLA AGM |  | Choose a type | Required String Size | 4 |  | To meet DC System voltage
Battery Name/Type | Xtender |  |  | Required Number of Parallel Strings | 2 |  | Should not exceed 3 or 4 strings
Battery Voltage | 6 | V |  | Battery Capacity | 620 | Ah | at 8 C-Rate
Battery Capacity | 310 | Ah |  | Battery Capacity | 14880 | Wh
Battery Hour Rate at Capacity | 8 | hr |  | Maximum Discharge Rate | 45.1757 | hr | Should not be less than 8-hr rate
DC System Voltage | 24 | V | Nominal Voltage of batteries | Maximum Discharge Rate | 0.022136 | C-Rate | Should not be more than 0.13
Desired Battery DOD | 0.5 |  | 0.5 typical for Lead-Acid
Days of Autonomy | 3 | days | 3 typical for solar only, 1 or 2 if other generation sources are available
PV Module Specifications |  |  |  | PV Module Requirements
| Entry | Units | Notes |  | Entry | Units | Notes
Module Name/Type | Canadian Solar |  |  | Adjusted Voc Extreme Min. Temp | 40.8679 | V | Determines Max in series
Rated Power | 250 | W | STC | Maximum String Size | 2 |  | Based on Max Input Voltage
Module Voc | 37.2 | V | Open Circuit Voltage | Maximum Strings in Parallel | 4 |  | Based on Max Input Current
Module Vmp | 30.1 | V | Max Power Voltage | Maximum Number of Modules | 4 |  | Based on Max Input Power
Module Isc | 8.87 | A | Short Circuit Current | Required fused combiner box? | N |  | To prevent back feeding
Module Imp | 8.3 | A | Max Power Current | Min Solar Power for Winter | 803.8847 | W | To prevent damage to batteries
Module Series Fuse Rating | 15 | A |  | Excess Summer Power | 4.0997 | kWh | Potentially unused daytime power during summer
Voc Correction (TCVoc) | -0.34% | %/°C | -0.4% Typical | Number of Modules | 4
Pmax Correction (TCPmax) | -0.43% | %/°C | -0.4% Typical | Adjusted Max Power of Array | 1124.7 | W | CC will limit to 1100W. This will not harm the controller. Do not exceed Voc
Desired PV String Size | 2 |  |  | STC Rating of Array | 1000 | W
Desired Number of Parallel PV Strings | 2
System Requirements
Charge Controller Specifications |  |  |  |  | Entry | Units | Notes
| Entry | Units | Notes | AC Derate Factor | 0.9108
Charge Controller Name/Type | ProStar MPPT |  |  | AC Peak Current | 13.7242 | A | Maximum continuous current
Maximum Input Voltage | 120 | V | Usually higher for MPPT | Rated Isc for PV Array | 17.74 | A
Maximum Input Current | 40 | A |  | Max system voltage (Voc low temp adj.) | 81.7358 | V
Maximum Input Power | 1100 | WDC |  | Rated MPP voltage( Typ. Op. Vmp) | 60.2 | V
|  |  |  | Maximum short circuit current | 22.175 | A
Inverter Specifications |  |  |  | MPP current (Imp for array) | 16.6 | A
| Entry | Units | Notes
Inverter Name/Type | PST-1000
DC Voltage | 24 | VAC
AC Voltage | 120 | VAC
Inverter Continuous Power | 1500 | W
Inverter Surge Power | 3000 | W
AC Overcurrent Protection | 20 | A

## 4 System Summary
Location Details
Location Name | Oakland
Extreme Minimum Temp in °C | -4°C
AC Load
Peak Continuous Power | 600 W
Peak Surge Power | 1500 W
Daily Energy Usage | 1470 kWh
Battery: VRLA AGM Xtender
Nominal Voltage | 6 V
Capacity | 310 Ah @ 8 C-Rate
Batteries in series | 4
Serial strings in parallel | 2
Total Capacity (Wh) | 14711 Wh
Charge Controller: ProStar MPPT
Battery System Voltage | 24 V
Maximum Input Voltage | 120V
Maximum Current | 40A
Inverter: PST-1000
Max Continuous Power | 1500W
Max Surge Power | 3000W
AC Overcurrent Protection | 20A
PV Module: Canadian Solar
Max Power (STC) | 250W
Open circuit voltage, Voc | 37.2V
Maximum power point voltage, Vmp | 30.1V
Short circuit current, Isc | 8.87A
Maximum power point current, Imp | 8.3A
Adjusted Voc Extreme Min. Temp | 40.87 V
PV Array
Modules in series | 2
Serial strings in parallel | 2
Total PV Power (STC) | 1000 W
Rated Isc for PV Array | 17.74 A
Max system voltage (Voc low temp adj.) | 81.74 V
Rated MPP voltage( Typ. Op. Vmp) | 60.2 V
Maximum short circuit current | 22.2 A
MPP current (Imp for array) | 16.6 A

## Questions (hidden)
C | Pole Mount | Flooded Lead-Acid
F | Rack Mount | VRLA AGM
| Roof Mount | VRLA Gel
Lithium-Ion
-4 | C
-4 | C